| Document control 2023s1457 Pen Caer Lan Solar Farm |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Contributing designers | Revision | Purpose of issue | Checked | Reviewed | Date |
| Charlotte Lickman | P01 | Planning | JP |  |  |

| Health and Safety Considerations |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Stage 1 Identify |  |  |  | Stage 2 Eliminate / Reduce | Stage 3 Inform |  | Stage 4 Control |  |
| Ref. no. | Project element, material or activity | Key health and safety hazards and their possible effects | People/ environment at risk from the hazard | Design measures taken to eliminate the hazard or reduce the risk | Significant residual hazards and risks | Communication method | Risk owner(s) | Proposed control measures |
| Guidance | Consider all aspects involved in each stage of interface with the site, environment and structure(s). | Record the key hazards and their potential consequences. | Identify the categories of people at risk. | Include obtaining adequate data for design certainty and any further studies carried out during the risk evaluation process. Proposed measures to be taken by constructors and operators are to be included in Stage 4. | Provide details of residual hazards and risks that will need to be communicated and managed. | Record how information is provided, whether on drawings, pre-construction information, buildability statement, specification, reports or H&S File | Record the name of designers, contractors, the client or other stakeholders who are to ensure the significant residual risk is minimised and controlled. | Recommend measures to be taken by the risk owner(s) to minimise and control the significant residual risk. |
| # Design |  |  |  |  |  |  |  |  |
| Des1 | Design of drainage (All sites) | Risk of striking services. Potential for underground services crossing the site - gas, electricity, process drains and surface water drains. | Site personnel. Existing infrastructure | Hazard cannot be eliminated by design. Available information should be reviewed and mapped. | Potential unidentified services | DRA | Designer at detailed stage (identifying known risks) Contractor (construction of the scheme) | Detailed survey of services prior to construction. Liaison with utility providers. Risk assessments and method statements and adequate briefing of site personnel. |
| Des2 | Design of drainage (All sites) | Ground and groundwater conditions: unknown at present however indicative information suggests that groundwater us unlikely to be a flood risk. Potential for: Contamination Instability Groundwater in excavations | Site personnel Site transformers and DNO substation compound | Hazard cannot be eliminated by design. Preliminary drainage design assumes largely shallow drainage / SuDS features. | Unknown ground conditions remain | DRA | Designer (identifying known risks) Contractor (construction of the scheme) | Follow recommendations arising from ground investigation report. |
| Des3 | Design of drainage (All sites) | Unexploded ordnance | Site personnel Site transformers and DNO substation compound | An unexploded ordnance map has been consulted at zeticauxo.com This has highlighted that there is a low risk of finding UXO across the proposed development site. | Low risk from UXO | DRA | Designer (identifying known risks) Contractor (construction of the scheme) | Risk assessments and method statements and adequate briefing of site personnel. |
| Des4 | Design of above ground SUDS features | Risk of trips and falls, drowning | Site personnel | Preliminary design undertaken in accordance with CIRIA C753. SuDS proposed include a shallow swale feature with 1:3 side slopes to allow for safe access/egress. | Lack of knowledge about the SuDS features. Disrepair/lack of maintenance causing instability or obscured visibility | DRA | Owner/operator/ scheme designer | Detailed design should consider the location of swales near to vehicular access routes to reduce the risk of vehicles entering SuDS assets. Passive surveillance on all above ground SuDS features is good due to the presence of roads and well-used footpaths and good visibility. Side slopes on features are a maximum of 1:3. Maintenance schedule to be prepared. |
| # Construction |  |  |  |  |  |  |  |  |
| Con1 | Excavations | Potential for instability of excavations Potential for striking of services | Site personnel Site transformers and DNO substation compound | Hazard cannot be eliminate. Limit depth of excavations where practicable. Ground investigations required. | Ground conditions and potential services. | DRA | Contractor | Early involvement of temporary works designer recommended Risk assessments and method statements and adequate briefing of site personnel. Follow recommendations arising from ground investigation report. Detailed survey of services prior to construction. Liaison with utility providers. |
| Con2 | Plant/ material deliveries | Access via A4109 and then the existing / proposed access track to the main site entrance. Unauthorised access by members of public. | Site personnel Public | Hazard cannot be eliminated by design. | Site access | DRA | Contractor | Traffic management plans, consultations with stakeholders, traffic management design and relevant NRSWA applications. Consider access to sites and expected levels of traffic, road widths, parking arrangements etc. Limit volumes of imported material or muck away where possible. Risk assessments and method statements and adequate briefing of site personnel. |
| Con 3 | Connection of the drainage system to the surface water body | Striking of services Contamination Instable excavation | Site personnel | Hazard cannot be eliminated by design. Limit depth of excavation where possible. | Water | DRA | Contractor | Edge barriers/ safety harnesses to be used. The work to be undertaken during dry weather periods. |
| # Operation & Maintenance |  |  |  |  |  |  |  |  |
| O&M1 | Drainage system in operation | Potential for failure of the drainage system and flooding of the site | Maintenance personnel | Design drainage to an appropriate design life and design storm event Consideration given appropriate arrangements for operation, maintenance and cleansing of features | Risk of flooding remains during exceedance events and if maintenance requirements are not followed. | Operation and maintenance manual (to be prepared) | Asset owner/operator | Regular maintenance in accordance with O&M manual, normal site safety controls, designated overland flow routes away from proposed DNO substation compound. |
| O&M2 | Maintenance of drainage system | Water | Maintenance personnel | Above ground shallow SuDS features recommended where possible. | Water | Operation and maintenance manual (to be prepared) | Asset owner/operator | Vegetation in swales should be cut using a strimmer rather than a mover due to the slope. Regular maintenance in accordance with O&M manual, normal site safety controls. |

| Environmental Considerations |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Stage 1 Identify |  |  |  | Stage 2 Eliminate / Reduce | Stage 3 Inform |  | Stage 4 Control |  |
| Ref. no. | Project element, material or activity | Key environmental hazards and their possible effects | Who or what is at risk from the hazard | Design measures taken to eliminate the hazard or reduce the risk | Significant residual hazards and risks | Communication method | Risk owner(s) | Proposed control measures |
| Guidance | Consider all aspects involved in each stage of interface with the site, environment and structure(s). | Record the key hazards and their potential consequences. | Identify the categories of people, animals or environments at risk. | Include obtaining adequate data for design certainty and any further studies carried out during the risk evaluation process. Proposed measures to be taken by constructors and operators are to be included in Stage 4. | Provide details of residual hazards and risks that will need to be communicated and managed. | Record how information is provided, whether on drawings, pre-construction information, buildability statement, specification, reports or H&S File | Record the name of designers, contractors, the client or other stakeholders who are to ensure the significant residual risk is minimised and controlled. | Recommend measures to be taken by the risk owner(s) to minimise and control the significant residual risk. |
| # Design |  |  |  |  |  |  |  |  |
| EDes1 | Design of drainage system | Potential for ground contamination, Risk of pollution | Groundwater / surface water bodies | Ground investigations to be undertaken prior to work beginning to assess any contaminants at the site. | N/A | DRA | Contractor | Ground investigation to be undertaken to assess the risk of ground contamination, and any remediation measures needed in order to mitigate risk of mobilisation of contaminants. |
| EDes2 | Design of drainage system | Oil spillage Pollution | Groundwater/ surface water bodies | SUDS have been used to treat flows. The Simple Index Approach has been utilised to demonstrate that the proposed SuDS features provide sufficient treatment to ensure there is no detrimental effect to water quality. Therefore, the SUDS measures are considered sufficient to control pollution within the development. | Lack of maintenance of SUDS features may mean pollution events bypass the SUDS features and pollute groundwater and/or the Ordinary Watercourses near to the site. | O&M manual | Asset owner/operator | Regular maintenance in accordance with O&M manual. |
| # Construction |  |  |  |  |  |  |  |  |
| Con1 | Construction of drainage system | Pollution of watercourses/drainage systems during construction, with sediments, oils and chemicals | Water bodies | Hazard cannot be eliminated by design. | Pollution | Construction Management Plan (to be prepared) | Contractor | Risk assessment and method statement undertaken to avoid pollution during the works. Water from excavations not to be connected to the drainage system. Use of silt curtains, bunded storage tanks, spill kits envisaged. |
| # Operation & Maintenance |  |  |  |  |  |  |  |  |
| O&M1 | Inspection and clearance of manholes/ basins/ swales | Oil/fuel, sediment Pollution | Environment Maintenance personnel | Hazard cannot be eliminated by design. | Pollution | Operation and maintenance manual (to be prepared) | Asset owner/operator | Regular maintenance in accordance with O&M manual, normal site safety controls. Materials/sediments removed to be treated as contaminated and disposed of to a licenced waste management facility |